## PREAMBLE
DIVISION NO.0 PREAMBLE TO BILL OF QUANTITIES:
Site Familiarization
Tenderers are highly encouraged to visit the site to become acquainted with the surroundings, take any necessary measurements, and ascertain the location of required access onto the site and the location of allowance for complying with the requirements and for the reinstatement to original condition of all roads and areas used or disturbed.
Contractor-Provided Facilities and Services
• The contractor shall provide at their own cost:
- Site offices, sheds, ground slabs, equipment, and furniture for both supervision and the contractor.
- Preparing access roads during construction.
- Storage areas.
- Workshop areas.
- Protection work like fences.
- All safety precautions, including health, safety, environment, and security (HSES) measures.
- All necessary work to protect people from construction activities.
General Contractor Responsibilities
• The contractor shall liaise and coordinate with the required authorities during the execution of the works.
• Prepare a closing plan for the construction site and obtain engineer approval before commencing work.
• The contractor shall ensure minimal inconvenience to third parties during construction and take special care to protect existing surroundings.
• Submit detailed shop drawings for all activities for engineer approval.
• Before commencing work, supply all required materials as specified and subject to engineer approval.
• Fix, maintain, and replace any underground services that may be damaged during work.
• Follow all engineer instructions, drawings, and specifications.
• Obtain approval for the benchmark and leveling network before excavation works.
• Comply with all local health and safety regulations.
• All training works for all supplied systems under this Contract shall be the sole responsibility of the Contractor. The Contractor shall submit a Training Plan for approval by YGAPC, and upon approval shall carry out and complete all training in accordance with the approved plan.
• Dispose of construction waste at a designated location and bear associated fees.
• Throughout the project, the contractor shall provide and maintain protection for adjacent properties, including:
- Protection from damage.
- Dust control measures with all necessary materials.
- Sound control measures to minimize noise from demolition activities.
Materials and Workmanship
• All materials used must be:
- New and of the best available quality, subject to Employer/Engineer approval.
- Durable and guaranteed.
- Not liable to any base exchange.
- Manufactured according to applicable standards.
• Workmanship must be:
- Approved by the Employer/Engineer.
- Consistent with best available common practice in engineering codes at the time of execution.
• Materials or products of a specific make or manufacturer are used as samples of what will be required. With Employer/Engineer approval, the Contractor may offer similar products from other manufacturers if the equivalent quality is guaranteed. In this case, the Contractor must submit a description and/or drawings showing all technical specifications, characteristics, make, type, and manufacturer address of the alternative materials.
Measurement:
• All activities mentioned in the BOQ will be measured by accurate field measurement, deducting all voids or openings to calculate a net volume or area (no exceptions).
• The contractor must adhere to the quantities provided and not carry out additional work without prior written approval from the Employer and Engineer. The quantities are not guaranteed, and any claims for cost or extra expenses due to quantity increase or decrease will not be accepted unless otherwise stipulated in the Contract.
Prices
• The Unit Prices in the BOQ include all operations for execution, completion, testing, finishes, fixtures, accessories, and appurtenances for the work, as specified or described in the Tender Documents. This includes any additions, deductions, or alterations made during construction.
• The Unit Price covers all costs, including:
- Additional site installations.
- Relocation.
- Supervision.
- Labor.
- Transportation and supply of materials.
- Provision, maintenance, use, and repair of plant, equipment, and appliances.
- Construction and maintenance of temporary works.
- Performance of all services.
- Performance of all services.
- Fulfillment of all obligations and responsibilities defined in the Contract.
• The Tenderer is deemed to have considered all conditions, obligations, and requirements before entering unit prices in the BOQ.
• The Unit Prices include:
- Erection, installation, fixing, and re-fixing of all elements.
- Visas for labor, gate passes.
Abbreviations:
The following abbreviations are used throughout the Bills of Quantities: – BoQs: Bills of Quantities. – MM: Millimeter. – CM: Centimeter. – L.M. OR M: Linear Meter. – M²: Square Meter. – M³: Cubic Meter. – L.S: Lump Sum. – NO: Number. – Kg: Kilogram. – REF: Reference.
Main Columns Supply and Construct Steel Columns of Hot Rolled Sections (IPE450) (H=4500 mm,B=190mm, tf=14.6mm, tw=9.4mm) including base plates (500x250x15), grouting and M16 anchor bolts, grade 8.8 and 600 mm length, as pre detail drawings and specification and painting as specified.
Wind Columns Supply and Construct Steel Columns of Hot Rolled HEA200 Sections (H=190 mm,B=200 mm, tf=10 mm, tw=6.5 mm) including base plates (250x250x12), grouting and M16 anchor bolts grade 8.8 and 450 mm length as pre detail drawings and specification and painting as specified.

## 01-ARCH & CIV
DIVISION NO.1 BOQ For Architectural & Civil Works for Upgrading of the Main Slipway Winch System
Item NO | DESCRIPTION | UNIT | QTY | UNIT PRICE (USD) | TOTAL COST (USD)
1.0 GENERAL NOTES 1.1. This Preamble and the associated Notes shall be read in conjunction with all other contract documents, including but not limited to the Conditions of Contract, General and Particular Technical Specifications, and all issued Construction Drawings (DWGs). 1.2. The descriptions of items in this Bill of Quantities (BOQ) are generally brief. The Contractor's rates and prices shall be deemed to be fully inclusive of all labour, materials, plant, equipment, tools, transport, temporary works, supervision, testing, all associated costs, overheads, and profit required to execute and complete the works as described in the contract documents, including full compliance with the Specifications and Drawings. 1.3. Unless explicitly stated otherwise, all works shall be executed in accordance with the latest relevant local regulations, national standards, and internationally accepted codes of practice. 1.4. The Contractor shall be deemed to have visited and inspected the site and its surroundings to have satisfied himself completely as to the nature of the ground and sub-soil, the form and nature of the site, the extent and nature of the work and materials necessary for the completion of the works, the means of access to the site, and any other matter, condition, or contingency which may affect his tender. No claims arising from a failure to do so will be considered. 1.5. The Contractor shall provide, erect, and maintain all necessary protection for the public, adjacent properties, and the works themselves. This includes, but is not limited to, fencing, hoarding, dust control measures, noise abatement, and all required safety precautions in compliance with Health, Safety, Environment, and Community (HSEC) standards. 1.6. The Contractor shall take all necessary precautions to minimize inconvenience to third parties and shall maintain the site and surrounding areas in a clean and orderly condition throughout the contract period.
1.7. Any dismantled items deemed reusable or serviceable by the Engineer shall be carefully removed, inventoried, and handed over to the Employer's designated representative (e.g., facility management). Rates shall include for this careful dismantling and handling. 1.8. All work shall be carried out in conformity with all local and national Health and Safety Regulations. The Contractor shall be solely responsible for all costs associated with compliance.
2.0 PRELIMINARIES & MOBILIZATION 2.1. The Contractor's rates for Mobilization & Demobilization shall be deemed to include, but are not limited to, the following: • Preparation and maintenance of temporary access roads, storage yards, and port areas required for the execution of the works. • Preparation and submission of a comprehensive Site Closing Plan for the Engineer's approval prior to the commencement of any demobilization activities. • Upon completion, the complete dismantling and removal from site of all temporary facilities, services, equipment, and surplus materials, leaving the site clean and tidy to the satisfaction of the Engineer.
1.1 | Rehabilitation of the Existing Wrench Room
| The prices of all rates below must include all dismantling and preparation work, including the removal of all doors, windows, and metal roofing cladding of the two rooms, and their delivery to the beneficiary's warehouses. The rate includes repairing and making good all damage resulting from the dismantling work. | Note.
1.1.1 | Stairs, steps Form and cast Reinforced concrete C25 (25Mpa on cylinder test) at 28 days for stairs, steps (150 mm height x 300 mm wide), including all necessary works, complete as required and shown on drawings and as per specifications. The rate includes supply and build side walls (with foundations) adjacent to stairs and rampswhere indicated on drawings using all necessary reinforced concrete and finsh to match the surrounding The price also includes, steel reinforcement as indicated on drawings, formwork, additives, curing, excavation, backfilling, plastering and all necessary to compete the work according to the Engineer's instructions. | M3 | 5
1.1.2 | External Plastering for Walls: Supply and install four-coat external plastering on all room exterior walls surfaces. The application system requires: a rough nail rendering (cement:sand 1:1); a second layer of 5mm-thick mortar (cement:sand 1:2); a subsequent 13mm-thick Undercoat (cement:sand 1:3); and a final Finishing Coat applied to achieve a smooth surface using a cement-sand mix (1:1). The work includes properly preparing the exterior surface of the walls, removing existing paint, scratch the surfaces, and making the surface ready to receive the cement plastering. The rate shall include all necessary materials, labor, metal lath or wire mesh at stress points and dissimilar joints, temporary protection, scaffolding, and full adherence to all dimensional, aesthetic, and technical requirements set forth by the drawings and specifications. | M2 | 240
1.1.3 | Epoxy Coating for Walls: Supply and apply a seamless, solvent-free epoxy polysulfide coating to internal surfaces to achieve a minimum 300 microns dry film thickness, with high chemical and abrasion resistance. The rate shall include for all necessary surface preparation, making good minor defects, application of a primer and multi-coat system by skilled applicators to achieve a smooth, uniform finish in an approved colour, submission of product data, and protection of the finished coating, all as per the manufacturer's instructions and to the Engineer's approval. | M2 | 199.5
1.1.4 | Epoxy Flooring: Supply and apply a heavy-duty, solvent-free, non-toxic, water-dispersed epoxy polysulfide flooring system to the RC slab-on-grade floor, designed to provide high resistance to chemicals, oils, petrol, water, heavy abrasion, and hot tyres, achieving a minimum total DFT of 1500 microns. The rate shall be comprehensive and include for all labour, tools, and equipment; submitting manufacturer's technical data, samples, and a detailed method statement for the Engineer's approval; thorough surface preparation of the concrete substrate, including but not limited to, removal of all laitance, grease, and contaminants via approved methods such as light grit blasting, surface grinding, or acid etching to achieve a sound and profiled surface; application of a compatible epoxy primer; and the subsequent application of the multi-coat epoxy system by trained and qualified workmen in strict accordance with the approved manufacturer's recommendations. The final finish shall be non-slip to a rating approved by the Engineer. The rate must also include for the protection of the finished surface from damage until the final handover of the works, all in complete accordance with the Specifications. | M² | 110
1.1.5 | External Waterproof Acrylic Granite Coating Supply and apply a heavy-duty, spray-applied acrylic granite coating to all designated external plastered wall surfaces of the winch room as detailed on the architectural drawings. The coating shall be comprised of colored natural quartz aggregates permanently bonded in a 100% pure acrylic polymer resin, specifically formulated for high durability and exceptional resistance to weathering, UV degradation, salt spray, fungal growth, and abrasion, making it suitable for a C5-M (very high marine) corrosive environment. The work shall include for all necessary surface preparation of the plaster substrate, including cleaning of all dust, debris, and efflorescence, followed by the application of a compatible penetrating acrylic primer/sealer as per the manufacturer's strict technical specifications to ensure permanent adhesion. The granite coating shall be spray-applied by approved specialist applicators to achieve a uniform texture and thickness. The final color and aggregate mix shall be selected from the approved manufacturer's catalog and is subject to final approval by the Engineer based on a minimum 1m² sample site sample panel. The rate shall be fully inclusive of all materials, labor, specialized equipment, scaffolding, surface preparation, primers, masking and protection of adjacent surfaces (windows, doors, etc.), and final site cleanup. | M2 | 240
1.1.6 | Steel Sliding Door: Supply, fabrication, and installation of a complete, heavy-duty, multi-leaf, Industrial Steel Sliding Door System, of an Engineer-approved make. The door leaves shall be robustly constructed from double-skinned, galvanized steel panels with a minimum sheet thickness of 2.0mm and an overall thickness of ≥80mm, featuring an insulating PU foam core. Operation shall be managed by a robust top-hung guiding system or bottom-supported rolling system incorporating heavy-duty sealed-bearing rollers running on a reinforced bottom track, and a steel top track for lateral guidance, ensuring smooth, stable movement and a clear, trip-free threshold. The scope includes provisions for manual operation utilizing heavy-duty grab handles. The final finish must comprise the galvanization, sanding, priming, puttying, applying 2 epoxy coats of metallic, and fixing properly using anti-rust anchors, completed fully in accordance with all specifications and the Engineer's instructions. | M² | 13.75
1.1.7 | Steel doors: Supply, installation and finishing of single and double leaf doors, comprising of steel tubes 50 mm X 25 mm X 2 mm attached and welded vertically in proper technical way, and tubes of the frames 50 mm X 50 mm X 5 mm. The work includes, providing and installing all required hardware and accessories (4hinges/side, locks, handles, ... etc.)of high quality, sanding, priming, puttying, applying 2 epoxy coats of metallic, fixing properly using anti-rust anchors , repairing any damages and finishing properly around the doors,, and all necessary related works, complete as shown on drawings, specifications and as per Engineer's instructions | M² | 13.2
1.1.8 | Aluminum windows. Supply and install Powder Coated Aluminum Hopper (bottom-hung) windows with profile thickness not less than 1.5 mm. Complete with openable sash with double glass layers 12mm total thick. The price includes fly screens, anchoring, and all accessories such as hinges, handles, latches, rubber EPDM, and sealing with silicone properly including all necessary related works, complete as shown on drawings, specifications and as per Engineers' instructions. | M² | 8.3
1.1.9 | UPVC/PVC Corrugated Roofing Sheets Supply, fabrication, and installation of complete shelter roof systems utilizing UPVC/PVC corrugated sheets, 3mm nominal thickness, complete with all necessary accessories and fixings. The corrugated sheets shall have a min 1000mm width, a min 6000mm standard length (or as required by layout), a 0.2mm minimum thickness protective layer, and a specified color. The material must possess superior properties including excellent thermal insulation with a maximum thermal conductivity coefficient of 0.08 W/(m⋅K), high climate, corrosion, impact, and tension resistance, and be fire retardant, warranting a minimum 10−year lifespan. The works shall include the supply and fabrication of 3mm thick pre-painted UPVC corrugated Ridge, Barge Eave, Corner Flashing, and Trims, appropriate self-drilling fasteners (SD5-5.5x25 and SL2-4.8x20), and Bead Mastic sealant for sealing roof panel end laps. The rate shall include all overlaping, and the contractor is responsible for all material, equipment, labor, sanding, repairing, and painting the metal parts of the roof, and temporary/permanent necessities required to complete the roof system in strict accordance with the Engineer's instructions. | M2 | 134
1.1.10 | 25 mm EPE Foam Insulation System: Supply, deliver, and install a 25 mm thick closed-cell Expanded Polyethylene (EPE) foam insulation system, laminated on both faces with high-reflectivity (95% minimum) aluminum foil. The material shall possess a maximum thermal conductivity of 0.034 W/m·K and a minimum tensile strength of 210.0 kPa. The scope includes installation beneath all specified external UPVC cladding (walls and roofs) in strict accordance with manufacturer's recommendations. All-inclusive rate covers approved marine-grade adhesives, mechanical fasteners, and the meticulous overlapping and sealing of all joints with premium aluminum-faced tape to establish a continuous thermal envelope and 100% vapor barrier. The rate shall include all overlapping, and the contractor is fully responsible for all material, equipment, labor, and all temporary or permanent works required to finish the work in strict compliance with the drawings, specifications, and the Engineer's instructions. | M2 | 134
1.1.11 | UPVC Gutter Supply and install Rectangular UPVC Gutter (200mm x 150mm) with 3mm thickness. The work includes providing and fixing all necessary components for a fully functional UPVC gutter system as per the drawings and Engineer's instructions. | L.M | 18.5
1.2 | PROJECT INFORMATION BOARD
1.2.1 | Marble Project Information Board: In number: The supply and installation of a marble panel for the project with dimensions (80 x 100 x 3) cm, fixed in a submerged form in the wall of the project and in a prominent place and at a higher level than the threshold of the ground floor. The name of the project and the supervisory authority and the name of the financing party (the grantor) should be written on it in sculpture ) and the year of implementation, and any other data and installation in the finishing stage and all that is needed to finish the item with the dimensions indicated in the drawings and specifications and according to the instructions of the supervising engineer. | No. | 1
1.2.2 | Project Name sign Board: Supply and installation of Project Information signboard: Supply, installation, and erection of project information signboard 3.1m height and 2.0m width, double-face, 5 slides, slides heights shall be as per drawing, The works include: 1) Unclassified excavation for R.C footings, Cut existing pavement using electrical saw,backfilling or borrow fill with compacting using suitable equipments,Hauling all disposal materials to approved location 2) Cast in situ reinforced concrete for footings 60x60 cm, (Cube Fc'=25MPa), conformed to ACI-318M codes requirements 3) Galvanized steel plates 3mm thick for the slides. 4) Galvanized steel pipes with a diameter of 63.5 mm and a thickness of 4 mm for posts. 5) Disposal and hauling of waste material to the approved location. 6) All works shall done according to drawings, specifications, and as directed by the engineer. | No. | 1
SUB TOTAL DIV-01

## 02-ELEC
DIVISION NO.2 BOQ for Electrical Works of Upgrading of the Main Slipway Winch System
Item NO | DESCRIPTION | UNIT | QTY | UNIT PRICE (USD) | TOTAL COST (USD)
| PREAMBLE - This section shall be read in conjunction with parts of (the Electrical Technical Specifications General and Particular) and the ELEC DWG, except where otherwise indicated. - The unit prices for all items in this section shall inclusive of supply, installation, selection, operation (commissioning) works and all other luxurious, accessories, appended and required. Therefore, the item will be fully inclusive, ready for use, with all its requirements, materials, and execution methods which the supervising engineer will demand, so as the item will become finally completed. Taking into consideration that all electrical wiring works must be hidden into the walls bodies, to the full satisfaction of UNDP Engineer. - In the event any item is not mentioned in this section and it is necessary or complementary of the work of another item already mentioned in the table of quantities, it is the contractor’s responsibility to provide all items without any additional cost. - All training works for all supplied systems under this Contract shall be the sole responsibility of the Contractor. The Contractor shall submit a Training Plan for approval by YGAPC, and upon approval shall carry out and complete all training in accordance with the approved plan. All costs related to training shall be included in the Contract Price. - Motor & VFD Validation: Conduct comprehensive performance tests for the 220 kW motor and 250 KW VFD to verify design power ratings, including the starting torque and pull-out torque capabilities. | Note.
2 | ELECTRICAL WORKS:
2.1 | DISTRIBUTION SYSTEM:
| Main and Sub-Main Distribution Boards: Supply, install, testing and commissionining of main distribution boards, (ABB, Legrand, Schneider, Hager or equivalent). In accordance with form-4 to BS EN 60439-3 (IEC 60439), IP-66 complete with all protective devices, measuring instruments, breakers, busbars, The main circuit breaker should equipped with an adjustable and advanced electronic protection unit (Microprocessor Trip Unit - L:Long-time, S:Short-time Delay, I: Instantaneous). Environmental and Anti-Condensation Control: To withstand the high humidity and ambient temperatures of the marine environment in Aden, the panel enclosure must feature factory-wired, thermostatically and hygrostatically controlled Anti-Condensation Space Heaters. Termination of incoming cables and outgoing bus duct including cable glands, labels, tags, terminations, components, pipes in recessed 25mm dia PVC pipe, all fittings (i.e. bends, thrust blocks, end caps, T-connections, reducers...etc.), cutting the wall to install DB, metal lathing 300 mm wide and 3.2 mm thickness shall be nailed and fixed over all grooves, plastering, hiding all cable pipes, accessories and all related ancillary works as shown on drawings and specified in specifications and in according to code of practice and standards such as IEC 60439,61439 and IEC 60947. | Note.
2.1.1 | MDB | No. | 1
| Final Distribution Boards : Supply, install, testing and commissionining of final distribution boards (panelboards) , (Legrand, Hager or equivalent). In accordance with form-4 to BS EN 60439-3(IEC 60439), IP-66 complete with all protective devices, measuring instruments, breakers, busbars, Termination of incoming cables and outgoing bus duct including cable glands, labels, tags, terminations, components, pipes in recessed 25mm dia PVC pipe, all fittings (i.e. bends, thrust blocks, end caps, T-connections, reducers...etc.), cutting the wall to install DB, metal lathing 300 mm wide and 3.2 mm thickness shall be nailed and fixed over all grooves, plastering, hiding all cable pipes, accessories and all related ancillary works as shown on drawings and specified in specifications and in according to code of practice and standards such as IEC 60439,61439 and IEC 60947. | Note.
2.1.2 | LP-DB | No. | 1
| HVAC Control Panel Boards : Supply, install, program, test, and commission one complete automatic Lead-Lag Control Panel for controlling the three split air-conditioning units serving the electrical equipment room. The panel shall provide automatic duty rotation, operating-hours equalization, adjustable staged operation, and Manual/Off/Auto control for each unit. The system shall include one wall-mounted room temperature sensor installed at an approved representative location. The controller shall sequentially start additional air-conditioning units at adjustable temperature setpoints and shall be capable of operating all three units simultaneously when required to maintain the specified room temperature. The panel shall be suitable for the high-humidity and salt-laden marine environment of Aden Port. The enclosure shall be manufactured from approved marine-grade GRP with a minimum IP65 protection rating and shall include corrosion-resistant components, stainless-steel fixings, IP-rated cable glands, and anti-condensation protection. The item shall include the programmable smart relay, temperature sensor, enclosure, interposing relays, protective devices, selector switches, status indication lamps, manufacturer-approved air-conditioning control interfaces, control wiring, conduits, labels, programming, testing, and all accessories required for a complete operational system. | Note.
2.1.3 | AC-DB | No. | 1
2.2 | L.V CABLES & CABLE WAY & Associated Civil/Infrastructure Works
| L.V CABLES: Supply, install, test and commission low voltage SWA/XLPE / PVC copper cables, (0.6/1K.V) including glands, cable ties, labeling, pipe (Saudi cable or equivalent) in cable tray, PVC pipe suitable size, all fittings (i.e. bends, thrust blocks, end caps, T-connections, reducers, cable glands...etc.), pipes as per drawings, hiding all pipes and cutting for cable pipes, metal lathing 300 mm wide and 3.2 mm thickness shall be nailed and fixed over all grooves, plastering, hiding all cable pipes, ducts, UPVC pipes , excavation, backfilling, laying on ground , Boxes, …etc. The item scope is fully comprehensive and shall include all necessary civil, structural, and mechanical installation works : Civil & Earthworks, Cable Trenches, Ducts & Containment, and Wall & Slab Concealment Works. All of which shall be according to the specifications, drawings. Codes of practice and highest prevailing engineering standards all associated according to the drawings, specifications and relevant codes of practice and highest prevailing engineering standards such as IEC 60502-1 and BS 6346,XLPE insulated and PVC seathed single or multi core flexible copper cables meeting IEC 60227 and IEC 60502; Cable ends connections are to be made through suitable lugs or terminals, crimped properly & with use of cable glands; for the following: | Note.
2.2.1 | 4C x 6 sqmm - CU / XLPE / PVC + E=6 sqmm. | L.M | 10
2.2.2 | 4C x 10 sqmm - CU / XLPE / PVC + E=10 sqmm. | L.M | 10
2.2.3 | 4C x 16 sqmm - CU / XLPE / SWA / PVC + E=16 sqmm. | L.M | 80
2.2.4 | 4C x 240 sqmm - CU / XLPE / PVC. | L.M | 20
2.2.5 | 2 X (4C x 240 sqmm - CU / XLPE / SWA / PVC) . | L.M | 170
| Main Earthing Cables: Single core cable for Earthing 1C - Cu / PVC. | Note.
2.2.6 | E = 1C x 240 sqmm - CU / PVC | L.M | 50
| Underground Cable Trench : Excavation (in all types of soil) of cable trench of cross section sizes mentioned hereinafter including shoring and shuttering works (If Required) and repave the excavated paved area if required to match the existing. The work shall include the following; - Supply an install UPVC pipes of sizes and numbers mentioned hereinafter, - Supply/import and lay approved sand bedding/covering materials (to be sieve sand) under (One layer, 15 cm thick) and over (Two layers, each 10cm thick). - Backfilling with excavated soil if suitable or imported soil if required with disposing surplus excavated soils outside the site. - Supply and install warning tape over the power and telecommuncation cables. - All required to complete the works according to technical specifications and instruction of site engineer. | Note.
2.2.7 | Trench of 80 cm width including 4 x 4" UPVC pipes | L.M | 100
2.2.8 | Trench of 40 cm width including 1 x 3" UPVC pipes | L.M | 55
| Inspection Manholes Supply, installation and testing of electrical Inspection manholes, of Internal dimension mentioned hereinafter. The rate shall include the following; - Excavation and backfilling works, - Supply and install plain concrete base (15 cm thick), - Supply and install concrete solid block walls (Solid concrete block size 20x20x40cm), - Supply and install Internal and external cement plastering for the manholes walls, - Supply and install heavy duty cast iron cover (20 tons Minimum). - All accessories needed and necessary installations to provide manholes for the electric power cables, according to technical specifications and instruction of site engineer. | Note.
2.2.9 | Manholes with dimention 80x80cm and 100cm depth. | No. | 10
2.3 | INDUSTRIAL SOCKETS PANEL BORAD IP-67 :
2.3.1 | Supply, install, testing and commissionining of complete Floor mounted 63 Amp INDUSTRIAL SOCKETS PANEL BORAD IP 67 , including: - 2 x 16A 240V 3-Pin Sockets - 1 x 16A 3P+N+E IP66 5-Pin Socket - 1 x 32A 3P+N+E IP66 5-Pin Socket - 4-Pole RCD 63A 30mA - 3-Pole Type C 16A Breaker - 3-Pole Type C 32A Breaker - 2 x 16A MCB And all fixings, supports, phase barriers, terminations and all related accessories according to the technical specifications, drawings, codes of practice and highest prevailing engineering standards. | No. | 2
2.4 | POWER SOCKETS AND ISOLATORS:
| POWER SOCKETS & OUTLET: Supply, install, testing and commissionining of complete socket outlet point or power point, including all conductors,cables 2x4sqmm+ 1x 4 sqmm (for cables of normal switches and sockets ), cables 2x6sqmm+ 1x 6 sqmm (for cables of industrial switches and sockets ), conduits, boxes, socket outlets and all related accessories according to the technical specifications, drawings, codes of practice and highest prevailing engineering standards. | Note.
2.4.1 | 13A, 230V, 2P+E simplex socket outlet British Standard. IP65. | No. | 4
2.4.2 | 13A, 230V, 2P+E duplex socket outlet British Standard. IP65. | No. | 2
2.4.3 | 45A, 230V, 2P+E duple Pole Switch. IP65. | No. | 3
2.4.4 | 40A, 230V, 2P+E heavy-duty industrial outlet for hvac unit. IP65 | No. | 3
2.5 | LIGHTING SYSTEM
2.5.1 | INTERNAL LIGHTING & FAN POINTS: Supply, install and connect commission complete lighting fixture with (4000 - 6000)K CCT, minimum 20000 hr. working lifetime, (100 - 120)lm/W luminous efficiency, RI>80% (Philips or equivalent) , hiding all pipes, pipes in recessed 25mm dia PVC, all fittings (i.e. bends, thrust blocks, end caps, T-connections, reducers...etc.), hiding all pipes and cutting for cable pipes, metal lathing 300 mm wide and 3.2 mm thickness shall be nailed and fixed over all grooves, plastering. The lighting fixtures shall be with 3x2.5 sq. mm PVC insulated multistring copper conductor cable (Saudi cable or equivalent), all supports, lamps, P.F. correction capacitors, electronic, connections, suspensions, clamps, switches single, double as per in the drawings, and all other accessories necessary to provide a complete fitting with all terminals and with all accessories to complete the work in according to drawings, specifications, international standards and code of practice such as IEC/EN 62471. | No. | 20
2.5.2 | MARINE EXTERNAL LIGHTING POINTS: Supply, install, terminate, test and commission complete marine-grade external lighting fixtures with (4000 - 6000)K CCT, minimum 20,000 hr. working lifetime (L70), (120 - 150) lm/W luminous efficacy, CRI >80, (Philips, Thorn or approved equivalent). Fixtures shall be complete with integral surge protection device (SPD), waterproof driver, corrosion-resistant marine-grade aluminum housing with anti-UV polyester powder coating, minimum IP66 / IK10 rating. All wiring shall be carried out using double-insulated, halogen-free, marine-approved flexible cables with tinned copper conductors, minimum 3x2.5 sq. mm (e.g. Prysmian, Nexans or approved equivalent), installed in heavy-duty galvanized rigid steel conduits (HD-GRS) with stainless steel 316 (SS316) fittings (including bends, inspection boxes, pull boxes, drain plugs, expansion couplings, watertight thread sealants and brass glands with IP68 rating). All conduits and accessories shall be hot-dip galvanized internally and externally. All cable trenches, excavations and backfilling shall include warning tape, sand bedding, protective concrete slabs, and mechanical protection where required. All conduits embedded in concrete or ground shall be pressure-tested for water tightness prior to pouring. Lighting fixtures shall be complete with all stainless steel 316 mounting brackets, anti-vibration supports, galvanized steel poles with marine-grade base plates, hot-dip galvanized anchor bolts, leveling nuts, grouting, earth rods (copper-bonded), earthing tapes, and all necessary clamping and connection accessories. Lighting Switches shall include single and double pole switches,and all other accessories necessary for full functional operation. All works shall be carried out in strict accordance with approved shop drawings, project specifications, international standards and marine installation practices such as IEC 60598-2-4 (for floodlights), IEC 61439 (for assemblies), IEC 60364-7-709 (for marinas), and IEC 62305 (lightning protection where applicable). | No. | 20
| LIGHTING FIXTURES: Supply, install, testing and commissionining of complete lighting fixture as shown on layout and discribed on legend complete with lamps and all related accessoriesas for the following: | Note.
| INTERNAL LIGHTING FIXTURES: | Note.
2.5.3 | Type F1 : Suspended high-bay lighting fixture with LED 40W, 5000lm, CRI ≥ 80, 4000-6000K, 50000h life, aluminum housing material, IP65. | No. | 14
2.5.4 | Type F7 : WALL MOUNTED EXIT SIGN LIGHTING LUMINAIRE, 5W LED AND WITH SINGLE SIDED PICTOGRAM, PROVIDED WITH BACKUP LITHIUM BATTERY OF 3 HOURS DURATION, IP44. | No. | 5
| EXTERNAL LIGHTING FIXTURES: | Note.
2.5.5 | Type F3 : HIGH QUALITY LED FLOOD OUTDOOR LIGHT, WALL MOUNTED FLOODLIGHT FIXTURE AND 60W, AT LEAST 6500lm, 5000K DAYLIGHT LED LAMP - IP65. | No. | 5
2.5.6 | Type F4 : HIGH QUALITY LED FLOOD OUTDOOR LIGHT, WALL MOUNTED FLOODLIGHT FIXTURE AND 200W AT LEAST 15000lm, 5000K, DAYLIGHT LED LAMP - IP66. | No. | 3
2.5.7 | Type F5 : WALL MOUNTED UNDERWATER MARINE LIGHTS, EOS FULL COLOR CHANGE (RGBW), SUPPLY VOLTAGE RANGE: 20 - 31 VDC, LUMENS: 39,375, BEAM ANGLE (DEGREES): 110°, HOUSING TYPE: MARINE GRADE ALUMINUM BRONZE, IP68. | No. | 12
2.6 | SAFETY AND SECURITY SYSTEMS
| CONVENTIONAL FIRE ALARM SYSTEM: Supply, install, testing and commissionining of complete Intelligent Conventional fire alarm system complete including shielded fire cable, conduits, boxes, junction derivation and outlet boxes, and all related accessories as the technical specifications and shown on the drawings and according to code of pratice and highest prevailing engineering standards and for the following: | Note.
2.6.1 | Conventional Fire Alarm Control Panel (FACP) - main control panel, 1 Zone consists of sheet steel cabinet, management system software, 72 hours battery back in standby mode and 30 min in alarm mode, up and all needed accessories.(all system devices should be UL, LPCB , or VdS certified). | No. | 1
2.6.2 | Multi-function smoke/heat detector. | No. | 4
2.6.3 | Resettable manual call point. | No. | 2
2.6.4 | Outdoor IP66 fire Alarm Bell with strobe (75dB) with flash lighting. | No. | 2
| IP SURVEILLANCE SYSTEM : Supply, install, testing and commissionining of complete IP Surveillance system with RJ45-Cat.6a cables, conduits fittings, junction boxes and all related accessories as specified and shown on the drawings for the following: | Note.
2.6.5 | Multifunctional Network Video Recorder 16 channels for real time viewing and recording @ 480/400fps including 2xHDD 10TB, PoE switch (1*24 ), patch panel 24 ports, and all related accessories. | No. | 1
2.6.6 | 42 inch smart color FHD Monitor. | No. | 1
2.6.7 | Indoor Dome Network Camera 6MP : Minimum Illumination: Color: 0.009 Lux @ (f/1.2, AGC ON), 12 VDC and PoE (802.3af) ,PAL / NTSC Picture format 1/3" interline Colour CCD Imaging device 530 TV lines or better Horizontal resolution 752 x 582 appx. 440,000 pixels Effective elements 0.1 lux or better in Colour mode Minimum illumination 48 db or better Signal to noise ratio,3.5 - 10.5 mm Illumination Distance : 30 m Variable focal lens Auto Iris control 530 TVL Resolution IP67 and IK10 protection UL/ CE/ FCC - Any two or more Certification | No. | 4
2.6.8 | Outdoor VF Bullet Network Camera 6MP: Minimum Illumination: Color: 0.009 Lux @ (f/1.2, AGC on), Main Stream: 30 fps (3200 × 1800, 3072 × 2048, 2560 × 1440, 1920 × 1080, 1280 × 720) EXIR 2.0 with up to 165 ft (60 m) IR Range 12 VDC and PoE (802.3af) Variable focal lens Auto Iris control IP67 and IK10 protection UL/ CE/ FCC - Any two or more Certification | No. | 6
| DATA EATHERNET NETWORK: Supply, install, testing and commissioning of complete main data Cabinet (DATA RACK) including data switches, patch panels, cable management, patch cords, data racks with suitable dimensions according to drawings and all related accessories, for the following: | Note.
2.6.9 | Data Cabinet including rack 9U , switch 24 port, patch panel 24 port, including Uplink FTP cat.7 cables between MDC and SDC. | No. | 1
2.7 | Power Supply Source and Protection
2.7.1 | Main Circuit Breaker (MCCB): Supply, install, testing and commissioning of complete Main Circuit Breaker for connection from utility power, including MCCB circuit breker 800A 4-pole 400V 50KA, 50Hz, enclosure, bus-bars, measurement instruments, all related accessories .All shall be in accordance with drawings, specifications, codes of practice and highest prevailing standards of engineering and as per the instruction of the supervised engineer. | No. | 1
2.8 | EARTHING AND BONDING SYSTEM
| Supply, install, test and commissioning of complete earthing system including ECC conductors, earth rodes, plates, investigation champer, clamps and all related accessories including bonding and terminations. Earthed equipontential bonding of all exposed and extraneous conductive parts. Earthing and bonding system for mechanical services including water Pumps, HVAC equipments, ...etc. . All of which shall be according to the technical specifications, drawings, codes of practice and highest prevailing engineering standards. | Note.
2.8.1 | Power Earth Unit including Galvanized earth rodes, investigation Champers, Marconite, earth bars, and all related accessories. (Earth Resistance not more than 5 Ohm) | No. | 3
2.8.2 | E: 1 x 120sqmm Earthing Conductor | L.M | 20
2.9 | LIGHTNING PROTECTION SYSTEM
| Supply, install, testing and commissionining of complete lightning Protection System, including air termination network, down conductors, test points, earthing pits, all related accessories. All of which shall be according to the technical specifications, drawings, codes of practice and highest prevailing engineering standards. | Note.
2.9.1 | Copper Tape 3x25mm . | L.M | 120
2.9.2 | 1x70sqmm Copper Conductor. | L.M | 20
2.9.3 | Early Streamer Emission (ESE) air terminal rod : ΔT=30µs 3 meters height. | No. | 1
2.9.4 | Earth Pit including Galvanized earth rode, investigation champer, bentonite, clamps and all related accessories. (Earth Resistance not more than 10 Ohm) | No. | 2
2.1 | Cathodic Protection System (Impressed Current Cathodic Protection ICCP)
| The bidder shall provide a complete price for every listed item. Unit rates shall include all materials, equipment, labour, marine and underwater access, tools, consumables, transport, supervision, overheads, profit and all incidental works necessary to complete the item. The bidder shall submit technical data sheets for the proposed equipment, an implementation programme, company profile and evidence of similar completed ICCP works. This is a non-payable general requirement; associated costs shall be distributed among the priced items. | Note.
| Supply, installation, testing, and commissioning of a complete operational Impressed Current Cathodic Protection system for the defined submerged and intermittently submerged steelwork of the main slipway, including all ICCP equipment and materials, underwater installation of anodes and reference electrodes, electrical works, cabling, junction boxes, control panel, bonding, earthing, necessary trenching and concrete works, system adjustment and optimisation, training, as-built drawings, operation and maintenance manuals, and warranty. The price shall include a pre-installation survey and detailed design by a qualified cathodic-protection specialist, covering protected surface area, coating condition, seawater resistivity, current demand, anode output and life, voltage drop, zoning, continuity, interference and final equipment sizing. This is a non-payable scope note; its requirements shall be included in the related priced items. | Note.
2.10.1 | ICCP ANODES
2.10.1.1 | Supply and installation of high-silicon cast-iron ICCP anode, nominal FeSiCr composition 14–16% silicon and 4–5% chromium, approximately 76 mm diameter × 1,525 mm long and 50 kg each, suitable for continuous seawater service, complete with factory-sealed cable entry and 6 m minimum continuous HMWPE-insulated marine cable, identification, traceable factory test certificate and manufacturer-declared current output and design life. Final suitability and quantity shall be confirmed by the approved ICCP design. | No. | 4
2.10.1.2 | Complete underwater anode connection and mounting assembly for each anode, including an approved watertight cable connector or resin-sealed junction pod where a joint is unavoidable, strain relief, protective cover, marine-grade mounting hardware, electrical insulation, and all accessories necessary for a mechanically secure and electrically sound installation. Submerged joints shall require prior approval. | Set | 4
2.10.2 | REFERENCE ELECTRODES
2.10.2.1 | Supply and installation of permanent silver/silver-chloride Ag/AgCl reference electrode, factory calibrated and suitable for continuous seawater immersion, approximately 32 mm diameter × 210 mm long, complete with minimum 10 m integral shielded marine cable, calibration certificate, insulated mounting bracket, SS316L protective cage, identification and all fixing accessories. | No. | 4
2.10.2.2 | Supply and installation of additional reference-electrode extension cable as required, low-noise twisted-pair shielded type with marine-grade HDPE/XLPE insulation and UV resistance, including approved watertight connections, glands, ferrules, terminals, identification and routing separately from power and VFD cables. The shield shall be terminated at one end only in accordance with the approved schematic to prevent ground loops. | L.M | 40
2.10.3 | CONTROL AND MONITORING EQUIPMENT
2.10.3.1 | Supply, installation, testing and commissioning of microprocessor-based ICCP control panel with not less than four independently monitored and controlled channels to match the four anode/reference zones. Panel shall provide automatic potential control and manual/constant-current operation, local display of individual channel voltage and current, data logging, adjustable alarms, reference-electrode failure protection, communications interface, circuit breakers, isolation transformer, surge protection, ventilation or anti-condensation heating, terminals and internal wiring. Tender basis shall be minimum 48 VDC and 3 A total output; final continuous output shall not be less than the approved calculated demand plus 25% spare capacity. Enclosure shall be minimum IP54 indoors and IP65 where exposed. | No. | 1
2.10.3.2 | Supply and installation of marine-grade SS316L waterproof junction box, approximate size 300 × 300 × 150 mm, minimum IP68 for the manufacturer-declared immersion depth and duration, complete with segregated terminals for anode-power and reference-signal circuits, tinned-copper terminal blocks, certified cable glands, blanking plugs, internal earth stud, labels and mounting hardware. | No. | 4
2.10.3.3 | Complete set of tinned-copper terminal blocks, lugs and connectors suitable for cables up to 35 mm², with insulated protective covers, ferrules, labels, fixing rail and all termination accessories. Materials shall be compatible with the connected conductors and marine environment. | Set | 4
2.10.4 | ELECTRICAL DISTRIBUTION EQUIPMENT
2.10.4.1 | Supply and installation of marine-grade SS316L waterproof junction box, approximate size 300 × 300 × 150 mm, minimum IP68 for the manufacturer-declared immersion depth and duration, complete with segregated terminals for anode-power and reference-signal circuits, tinned-copper terminal blocks, certified cable glands, blanking plugs, internal earth stud, labels and mounting hardware. | No. | 4
2.10.4.2 | Complete set of tinned-copper terminal blocks, lugs and connectors suitable for cables up to 35 mm², with insulated protective covers, ferrules, labels, fixing rail and all termination accessories. Materials shall be compatible with the connected conductors and marine environment. | Set | 4
2.10.5 | POWER CABLES & WIRING
| Supply, installation, testing and commissioning of complete single-core or multicore copper cables, including cable lugs, heat-shrink tubing, markers, glands, PVC or approved marine-grade conduit and fittings, clamps, cleats, supports, brackets, terminals, boxes, sleeves, excavation, selected backfilling, reinstatement and all accessories. Cable routes and segregation shall comply with the approved drawings and applicable standards. Rates for the following cables shall include all termination and testing works, together with surface preparation and application of compatible marine-grade, UV-resistant yellow route-marking paint, including primer where required and not less than two finish coats along the approved cable routes. This is a non-payable scope note and all associated costs shall be included in the cable unit rates. | Note.
2.10.5.1 | Anode positive feeder cable, minimum 10 mm² tinned-copper conductor with HMWPE/XLPE marine-grade and UV-resistant insulation, black or permanently identified as positive, including installation, mechanical protection, glands, lugs, terminations, markers, continuity and insulation-resistance testing. Final size shall comply with the approved ampacity and voltage-drop calculations. | L.M | 120
2.10.5.2 | Reference-cell signal cable, minimum 2.5 mm² low-noise twisted pair, individually shielded, with HDPE/XLPE marine-grade insulation, including installation, segregation from power cables, glands, terminals, labels and functional testing. Reference-electrode circuits shall not be subjected to insulation-test voltage unless expressly permitted by the manufacturer. | L.M | 80
2.10.5.3 | System negative-return and rail-bonding cable, minimum 35 mm² tinned-copper conductor with XLPE marine-grade insulation, including lugs, connection pads, test links where required, mechanical protection, identification and low-resistance continuity testing of every completed bond. Final size shall comply with the approved current and voltage-drop calculations. | L.M | 50
2.10.6 | INSTALLATION MATERIALS (ANODE MOUNTING HARDWARE)
2.10.6.1 | Supply, fabrication and installation of SS316L L-shaped mounting brackets/flat bars, nominal section 50 × 10 mm, including cutting, drilling, alignment, finishing, electrical isolation where required, and all above-water and underwater welding necessary for a complete installation. The unit rate shall include: a) Approved underwater wet-welding electrodes, nominal 3.2 mm diameter, selected to suit the verified parent metal and the approved WPS/PQR. SS316L welding consumables shall not be used on carbon steel unless supported by an approved welding procedure. b) Qualified welders/diver-welders, electrode storage and handling, welding plant, minimum 50 mm² flexible welding power and return cables, insulated electrode holder, return clamp, connectors and all required safety accessories. The return clamp shall be positioned close to the weld to prevent welding current from passing through bearings, electrical bonds or ICCP components. c) Protection and temporary isolation of ICCP and reference-electrode circuits during welding, visual inspection and specified NDT of completed welds. d) Surface preparation and complete reinstatement of the approved marine protective-coating system at all welds and disturbed locations, including compatible primer, intermediate and finish coats, dry-film thickness verification and all required touch-up repairs. e) All labour, equipment, tools, consumables, marine and underwater access and incidental works necessary to complete the installation in accordance with the approved mounting details. SS316 fastening bolts, nuts and washers are excluded from this item and shall be measured separately under Item 1.1.6.2. | L.M | 16
2.10.6.2 | SS316 fastening hardware comprising M12 × 50 mm bolts, nuts and washers, complete as one fastening set and including insulating sleeves/washers where required to prevent galvanic contact between dissimilar metals. | Set | 20
2.10.6.3 | Electrical isolation kit comprising marine-grade HDPE or G10 insulating washers, sleeves and bushes, complete for one anode mounting assembly and sized in accordance with the approved details. Electrical isolation shall be verified after installation. | Set | 4
2.10.6.4 | Supply of marine-grade anti-seize and anti-corrosion compound suitable for SS316/SS316L fastening assemblies and compatible with carbon steel, insulating materials and the marine environment, supplied in sealed tubes of not less than 500 g each. The compound shall be metal-free or nickel-based unless otherwise recommended by the fastening-system manufacturer and approved by the Engineer. Copper-based compounds shall not be used in contact with carbon steel or dissimilar-metal interfaces unless their compatibility is demonstrated and approved. | No. | 2
2.10.7 | GROUNDING SYSTEM MATERIALS
2.10.7.1 | Supply, install, test and commission one complete protective-earthing electrode assembly comprising one copper-bonded steel earth rod, minimum 16 mm diameter × 1.2 m long, approved bronze mechanical clamp or exothermic-welded connection, tinned-copper earthing conductor, inspection chamber, identification and 50 kg non-corrosive ground-enhancement material. Three assemblies shall be interconnected to form the ICCP protective-earthing system. The final combined earth resistance shall not exceed 5 ohms, or the lower value required by the authority or equipment manufacturer, verified by the three-point fall-of-potential method. The rate shall include additional rod depth or enhancement material necessary to achieve the specified value. Protective earth shall not be indiscriminately connected to the ICCP positive, reference-electrode or structure negative-return circuits. | No. | 3
2.10.8 | CIVIL WORKS MATERIALS
2.10.8.1 | Supply and place ready-mixed concrete, minimum characteristic compressive strength 25 MPa at 28 days, for approved anode, junction-box or equipment supports, including surface preparation, placing, compaction, curing and finishing. | m3 | 1
2.10.8.2 | Provide all formwork and reinforcement required for the concrete supports, including cutting, bending, tying, spacers, supports, removal of formwork and all incidental materials, in accordance with the approved details. This item is payable as one complete lump-sum scope. | L.S. | 1
2.10.8.3 | Supply and install engraved marine-grade aluminum warning and identification sign, approximate size 300 × 400 mm, with durable lettering, corrosion-resistant supports and SS316 fixing hardware, at the approved locations. | No. | 4
2.11 | WINCH MOTOR & VFD SUPPLY & INSTALLATION
| Supply, installation, testing, and commissioning of the complete WINCH MOTOR system with all related accessories All works shall comply with the technical specifications, approved drawings, applicable codes of practice, and relevant international standards (including IEC 60034 and IEC 60092) suitable for marine applications. | Note.
2.11.1 | SUPPLY, INSTALLATION, OPERATION & TESTING OF ELECTRIC MOTOR
2.11.1.1 | Supply, Install, Operation, Inspection, Testing and Final Commissioning of Customized Marine Electric AC induction Motor
| Motor Technical Data: - Power: ≥ 220 kW (295 HP),Voltage: 400V ±10%,3-phase,50Hz, Speed:1000 RPM (6-pole). - Construction: Squirrel-cage induction, IE4 premium efficiency (≥96.0%). - Duty Type: S1 (Continuous Duty), suitable for winch application and High Starting Torque. - Protection: IP65 recommended for marine port environment, high humidity and saline atmosphere, Anti-condensation space heaters. - Cooling method: IC416 —forced ventilation, independently powered cooling fan (per IEC 60034-6). - Temperature rise class: limited to Class B within Class F insulation. - Mounting: Foot-mounted. Final mounting arrangement to be confirmed after site verification. - Inverter-duty rating: IEC 60034-25 / NEMA MG1 Part 31 — reinforced winding insulation, withstands 1600 V peak. - Bearings: Heavy-duty rolling bearings, L10 ≥ 40,000 hr, PLUS insulated NDE bearing or shaft grounding ring (Aegis SGR or equivalent). - Thermal protection: 3 × PTC thermistors (one per phase) wired to VFD motor protection input. - Speed feedback: 1024 ppr incremental encoder, HTL output, NDE-shaft mounted (required for closed-loop control at creep duty). - Anti-condensation heater: 230 V single-phase, energized when motor stopped. - Starting Torque: 250% of rated torque, Pull-out Torque: 310% of rated torque. - Windings: Copper windings. | Set | 1
Other Requirements : - Shaft Voltage and Bearing Protection: motor shall be equipped with an Insulated Bearing at the Non-Drive End (NDE). - Motor shall be suitable for frequent start/stop operation and capable of withstanding high inertia loads typical for slipway winch applications and shall comply with DNV / Lloyd’s / ABS type approval where applicable; IEC 60034 and IEC 60092 (where applicable for marine applications). - Overload Protection via VFD and/or external motor protection relay, Embedded temperature sensors (PTC or PT100) in stator windings for thermal protection. - Factory routine tests in accordance with IEC 60034, including no-load test, insulation resistance and temperature rise test. Certificate of Origin and Test Reports shall be provided.
Motor Mechanical Data: -Frame Size: IEC 355 (to be verified on site to match existing baseplate and alignment). -Existing Motor Dimensions (For Reference): The contractor shall verify all of the following dimensions on-site prior to manufacturing: H: 43 cm, LC: 173 cm, AB: 78 cm, AC: 70 cm, A: 68.5 cm, B: 70 cm, EA: 25.5 cm. - Shaft Diameter: 9.25 cm , Shaft Length : 25.1 cm. (to be verified on site). - Heavy-duty rolling bearings suitable for winch application, minimum L10 life ≥ 40,000 hours. - Mechanical Compatibility: Shaft dimensions, keyway, tolerances, and mechanical strength shall be fully compatible with the existing brake system and gearbox coupling, and shall be verified on-site prior to manufacturing.
2.11.1.2 | Removal of Existing DC Motor and Base Modification.
| Remove the existing DC motor and all associated connections. Design, fabricate, supply, and install a heavy-duty adjustable motor base and any required mechanical elements to accommodate the new 220 kW AC motor, ensuring full integration with the existing slipway winch gearbox and braking system. The contractor shall be fully responsible for all works necessary to connect, align, and secure the new motor to the existing system, including any couplings, adapters, or modifications required for operational compatibility, proper alignment, and safe functioning. Method statements, shop drawings, and calculations shall be submitted for approval. All works, testing, and commissioning shall be completed to the satisfaction of the Engineer and YGAPC. | Set | 1
2.11.2 | Supply, Installation, Testing, and Commissioning of Complete 18-Pulse Variable Frequency Drive (VFD) System for 250 kW Marine Winch Motor
Supply, Installation, Commissioning, Programming and Operation of a complete 18-Pulse Diode Rectifier Variable Frequency Drive (VFD) system. The system shall be specifically designed for marine winch and hoisting applications in a port environment. Drive Specifications:
2.11.2.1 | - Rated power (HD / CT): 250 kW, 400 V, 3-phase Heavy-Duty (Constant Torque) VFD with Closed-loop flux vector control with encoder feedback. - Continuous output current: ≥ 415 A at 400V. - Overload capability: 150% overload capacity for 60 seconds, PLUS 180% for 3 second. - Front-end topology: 18-Pulse Diode Rectifier with Phase-Shifting Isolation Transformer. (see item 1.2.2.2) - Harmonic Distortion: Total Harmonic Current Distortion (THDi) shall be < 10% at full load at the Point of Common Coupling (PCC), ensuring strict compliance with IEEE 519-2014 standards. achieved inherently through the 18-pulse rectifier topology and phase-shifting transformer without additional active filters. - Braking method: Dynamic braking using external Braking Resistor (DBR) with integrated Braking Chopper module. (see items 1.2.2.3 and 1.2.2.4). - Braking Torque: Capable of providing 100% rated braking torque for a minimum of 60 seconds (intermittent duty cycle), with thermal protection and overload monitoring. - Hoist macro / firmware: hoist-crane firmware macro with mechanical-brake control output, torque-proving before brake release, anti-runback / load-float at zero speed. - Functional safety: Safe Torque Off (STO) to SIL 3 / PL d minimum per IEC 61508 / ISO 13849, integrated with hard-wired E-stop circuit. - Speed presets: Heavy-pull (12.78 Hz / 256 rpm), medium (17.5 Hz / 350 rpm), cradle return (selectable), creep (1.28 Hz / 25 rpm). - Acceleration profile: S-curve with adjustable jerk limit to control rope shock loading. - Output filtering: Heavy-duty dV/dt filter shall be strictly integrated at the VFD output to protect motor insulation from high voltage spikes. - Enclosure: IP55 floor-standing cabinet, with conformal coated PCBs (added for marine humidity), Forced air cooling with integrated cooling fans. - Communication: digital display, and communication interfaces (Modbus RTU + EtherNet/IP). | No. | 1
The scope of Work shall include: The Contractor's scope shall be comprehensive and shall include, but not be limited to: - Supply and delivery of the complete 18-Pulse VFD system with all internal components, including the rectifier module, DC bus, inverter module, braking chopper, dV/dt output filter, cooling fans, control electronics, enclosure, system grounding, and all necessary electrical cables and connections to the motor and main control. - Supply and installation of all associated external components (18-Pulse isolation transformer, dynamic braking resistors, thermal monitoring system — as per items 1.2.2.2 through 1.2.2.6). - Full programming, parameterization, and commissioning of the drive system. - Optimization of all control parameters (PI loops, ramp times, current limits, speed presets, S-curve profiles). - Functional testing under no-load and full-load conditions (simulated and actual) to verify performance. - Submission of comprehensive commissioning reports, as-built drawings, operation and maintenance manuals, and test certificates. - All works shall comply with relevant IEC standards (IEC 61800, IEC 60204, IEC 60529, IEC 61508, IEEE 519-2014) and marine application requirements. Deliverables: - Upon completion of installation and commissioning, the Contractor shall provide the following documentation: - Manufacturer's data sheets and technical catalogues. - Factory Acceptance Test (FAT) certificates and type test reports. - As-built electrical connection diagrams (Single Line Diagrams, Schematic Diagrams, Wiring Diagrams). - Detailed Commissioning Plan and Test Reports (including no-load and full-load tests). - Programming software and all parameter files (on CD/USB). - Warranty Certificate (minimum 24 months from date of Final Acceptance).
2.11.2.2 | Supply and Installation of 18-Pulse Phase-Shifting Isolation Transformer Supply, deliver, install, test, and commission a 18-Pulse Phase-Shifting Isolation Transformer specifically designed to feed the 18-Pulse Diode Rectifier VFD system. The transformer shall provide the necessary phase-shifted secondary windings to achieve the 18-pulse rectification and shall ensure electrical isolation between the mains supply and the drive Transformer Specifications: - Voltage: 400V ±10%, 3-phase, 50Hz - Secondary Voltage: 400V (with phase-shifted windings for 18-pulse operation) - Rated Power: ≥ 250 kVA - Cooling Method: Dry-type, forced air cooling as required. - Winding Configuration: Multi-winding secondary (typically 3 secondary windings, each phase-shifted by 20°, to achieve 18-pulse rectification). - Insulation Class: Class F (155°C) minimum. - Temperature Rise: Class B (80 K) temperature rise at rated load. - Degree of Protection: IP54 minimum (suitable for indoor, dusty and humid port environment). - Efficiency: ≥ 98% at full load. - Construction: Cast resin or VPI (Vacuum Pressure Impregnated) construction for high humidity resistance. - Standards: Compliant with IEC 60076, IEC 61558. | No. | 1
Scope of Work: - Supply and delivery of the transformer complete with all mounting brackets, terminals, and connection lugs. - Supply and Installation of MCCB / Fuse-switch for 18-Pulse Isolation Transformer primary and secondary protection. - Installation on a prepared foundation or floor-mounted base, including all structural supports and anchoring. - Primary and secondary electrical connections using appropriately rated copper cables, lugs, and cable glands. - Connection to VFD input terminals and mains distribution switchboard. - Earthing/grounding of the transformer core and frame in accordance with local and international standards. - Full testing and commissioning, including ratio test, insulation resistance test, polarity test, and load test. Compliance: - All works shall comply with relevant IEC standards (IEC 60076, IEC 61558) and marine application requirements.
2.11.2.3 | Supply and Installation of Dynamic Braking Chopper Module Supply, deliver, install, test, and commission a Dynamic Braking Chopper Module specifically designed for use with the 250 kW, 400V VFD system. The chopper shall be integrated into the VFD cabinet and shall be responsible for switching the braking resistor into the DC bus circuit when regenerative energy exceeds the bus voltage threshold. Chopper Specifications: - Voltage Rating: Suitable for nominal DC bus 540 – 565 V DC, with an adjustable activation threshold range of 670 – 780 V DC, and maximum DC withstand voltage of not less than 850 V DC. - Power Rating: Compatible with 250 kW VFD and 250 kW braking resistor assembly. - Duty Cycle: Heavy-duty continuous operation, capable of 100% continuous duty cycle (unrestricted continuous braking during prolonged slipway lowering operations). - Protection: Integrated overcurrent, overtemperature, short-circuit protection, dV/dt snubber protection, and DC overvoltage protection. - Control & Safety Interlocking: Automatic activation based on adjustable DC bus voltage threshold. Includes hardwired status/fault output contacts (NC/NO) integrated with the VFD safety chain and mechanical brake control circuit. - Status Indication: Local LED / display indication for chopper operational status and fault diagnostics. - Compatibility: Fully compatible with the supplied 250 kW 18-Pulse VFD and marine-grade DBR assembly. - Filtering : Integrated Snubber Circuit / dV/dt filter to suppress high-voltage spikes and electromagnetic interference (EMI) generated during high-frequency switching under full load. - Mounting: Factory-mounted inside the VFD cabinet (or supplied as a separate module if cabinet space is insufficient). | Set. | 1
The scope of Work shall include: - Supply and delivery of the chopper module complete with all mounting hardware and connection terminals. - Internal connection to the VFD DC bus within the main VFD cabinet. - Connection to the external dynamic braking resistor assembly. - Programming and configuration of chopper parameters (voltage thresholds, duty cycle limits, thermal protection). - Full functional testing of chopper operation during regenerative braking. Compliance: - All works shall comply with relevant IEC standards (IEC 61800-5-1, IEC 60204) and marine application requirements.
2.11.2.4 | Supply and Installation of Dynamic Braking Resistor (DBR) Assembly Supply, deliver, install, test, and commission a complete Dynamic Braking Resistor (DBR) Assembly, specifically designed to dissipate regenerative energy generated during braking of the 250 kW winch motor. The assembly shall be capable of absorbing peak braking power and dissipating thermal energy safely, without overheating or causing damage to surrounding equipment. Resistor Specifications: - Continuous Braking Power: ≥ 50 kW (continuous, capable of sustained operation at this power level). - Peak Braking Power: Heavy-duty continuous rating, minimum 250 kW continuous power capacity (100% continuous duty cycle for a minimum of 30 minutes uninterrupted lowering operations). - Resistance Value: As recommended by the VFD manufacturer (typically 2.0 – 3.0 Ω; exact value to be determined by the manufacturer based on VFD specifications). - Tolerance: ±5% of nominal resistance value. - Duty Cycle: S1 / Continuous regenerative duty cycle (specifically designed for overhauling marine slipway loads). - Enclosure: Outdoor marine-grade Heavy-Duty Stainless Steel 316L enclosure (minimum IP54 rated with louvered mesh protection and weather canopy). - Cooling System: Heavy-duty forced-air cooling with high-efficiency, marine-treated cooling fan(s), complete with airflow failure detection switches. - Thermal Protection: Integrated multi-stage thermal monitoring (including bimetallic/PT100 sensors) providing dry N/C contacts for alarm and hardwired VFD/Brake trip safety chain. - Resistor Element Material: High-grade stainless steel grid or nickel-chromium alloy resistor elements mounted on high-temperature ceramic insulators. - Terminals & Termination: Heavy-duty copper connection lugs, suitable for 2x(1x120mm² ) high-temperature power cables per polarity plus PE ground cable. | Set. | 1
The scope of Work shall include: - DBR assembly shall be installed outside the main control room, free-standing, floor-mounted on a dedicated concrete plinth with weather protection canopy and with all necessary support brackets and anchoring. - Minimum clearance of 500mm from walls and ceiling for adequate airflow and heat dissipation. - Supply and delivery of the complete DBR assembly, including enclosure, resistor elements, cooling fan, and thermal monitoring components. - Installation on prepared foundation/plinth, including all structural supports, anchoring, and vibration isolators. - Connection to the braking chopper module (output) using high-temperature rated cables (see item 1.2.2.5). - Connection of cooling fan power supply and thermal monitoring circuit to the control system. - Full functional testing of DBR operation during regenerative braking, including thermal protection verification. Compliance: - All works shall comply with relevant IEC standards (IEC 61800-5-1, IEC 60204, IEC 60529) and marine application requirements.
2.11.2.5 | Supply and Installation of High-Temperature Cables for Dynamic Braking Resistor Supply, deliver, install, and terminate high-temperature, heavy-duty power cables dedicated to connecting the 250 kW Dynamic Braking Chopper Module to the external Dynamic Braking Resistor (DBR) Assembly. The cables shall be specifically rated for continuous duty regenerative loads and designed to withstand thermal, mechanical, and electromagnetic stresses. Cable Specifications: - Type: High-temperature, single-core, flexible screened/shielded copper power cable. - Conductor Material: Class 5 stranded flexible tinned copper. - Cross-Sectional Area: Properly sized to continuously carry a minimum of 400 A DC, with a minimum size of 2 x (1 x 120 mm²) parallel runs per polarity. - Insulation Material: High-grade Silicone Rubber or EPR (Ethylene Propylene Rubber) insulation capable of continuous operation at ≥ 110°C, with short-term withstand capability of ≥ 180°C. - Shielding / EMI Protection: Copper wire braid screen / copper tape shield to prevent high-frequency Electromagnetic Interference (EMI/RFI) caused by high-power Chopper PWM switching. - Voltage Rating: 0.6/1 kV AC (rated for 1.5 kV DC insulation withstand level). - Core Color: Clear polarity identification (Red for DC+ and Black for BR/DC-). - Terminal Thermal Sleeving: Ends terminating at the DBR enclosure terminals shall be protected with high-temperature fiberglass/silicone heat-shrink sleeves to withstand radiative heat. - Mechanical Protection & Installation: Installed inside heavy-duty galvanized metallic conduits/flexible metallic liquid-tight conduits with brass EMC-compliant cable glands at both ends. - Earthing: Includes a dedicated PE grounding conductor (minimum 1 x 120 mm²) connecting the DBR metallic frame to the main VFD panel earth busbar. | L.M | 15
The scope of Work shall include: - Supply and delivery of high-temperature cables as specified, including all necessary cable lugs, glands, and marking/labelling. - Installation in appropriate cable trays, conduits, or trunking between the VFD cabinet and the DBR assembly. - Termination at both ends using high-temperature compression lugs (crimped). - Proper cable supports and clearances to prevent chafing or overheating due to proximity to hot surfaces. - Cable identification and labelling in accordance with project standards. Compliance: - All works shall comply with relevant IEC standards (IEC 60227, IEC 60502) and marine application requirements.
2.11.2.6 | Supply and Installation of Thermal Monitoring System for Dynamic Braking Resistor Supply, install, test, and commission a complete Thermal Monitoring System for the Dynamic Braking Resistor (DBR) Assembly. The system shall continuously monitor the temperature of the resistor elements and provide both alarm and trip signals to the PLC/VFD control system to prevent thermal overload and damage. System Specifications: - Sensors: Minimum 2 thermocouples (Type K) or PTC thermistors (as recommended by DBR manufacturer) installed at the hottest points of the resistor assembly. - Controller: Dedicated temperature controller (or integration with VFD/PLC analog inputs) with dual alarm/trip setpoints. - Display: Local digital display of temperature at the DBR assembly or remote display on the main control panel/HMI. - Alarm Output: N/O or N/C contact (dry contact) to PLC/VFD, programmable for pre-alarm and trip thresholds. - Trip Output: Hard-wired protection circuit to trip the VFD and activate main line contactor in case of overtemperature. - Reset: Manual reset after tripping to ensure safe restart. - Mounting: Sensors factory-installed on DBR; controller to be mounted inside or adjacent to the main VFD cabinet. | Set. | 1
The scope of Work shall include: - Supply and delivery of thermal sensors, controller, and all associated accessories. - Installation of sensors on the DBR assembly at manufacturer-specified locations. - Wiring of sensors to the temperature controller (shielded cables). - Wiring of control outputs (alarm and trip) to the VFD and/or PLC control system. Configuration and programming of temperature setpoints (alarm and trip) based on DBR manufacturer data. - Full functional testing of the thermal monitoring system, including simulation of overtemperature conditions to verify alarm and trip functions. - Issuance of calibration certificates and test reports. Compliance: - All works shall comply with relevant IEC standards (IEC 61508) and marine application requirements.
2.11.3 | SUPPLY, INSTALLATION, OPERATION & TESTING OF AUTOMATED CONTROL SYSTEM (PLC) & OPERATION INTERFACE
2.11.3.1 | Supply, installation, connection, programming, and commissioning of a PLC-based control system with a 10-inch HMI touchscreen, continuous monitoring, data logging, multi-level alarms, wireless remote control, and emergency stop buttons. All software, licenses, and programming shall be included. The works shall include: - Installation of the main control cabinet, sensors (load cell, speed, temperature, current transformers), emergency stop buttons along the slipway, pull-wire system, extension of all cables, and associated lighting and signaling systems. - Programming of operation interface, monitoring system, display screens, maintenance alarms, and testing of all circuits. - Issuance of fully programmed operation and maintenance manuals. - Environmental and Anti-Condensation Control: To withstand the high humidity and ambient temperatures of the marine environment in Aden, the panel enclosure must feature factory-wired, thermostatically and hygrostatically controlled Anti-Condensation Space Heaters. - All works shall comply with IEC 61131-3, IEC 61508 (where applicable), and marine standards. Full functional testing shall be performed prior to commissioning. | Set | 1
2.11.4 | ELECTRICAL WORKS & INTEGRATION WITH EXISTING SYSTEM
2.11.4.1 | Supply & Installation of Control Cables Supply and installation of multi-core shielded cables for sensors, signals, and control circuits, including all connections, plugs, terminations, and grounding. Cables shall be suitable for marine environments, with proper mechanical protection and compliance with relevant standards. | Set | 1
2.11.4.2 | Supply & Installation of Semiconductor fuses (VFD input) Supply and installation of Semiconductor fuses (VFD input, Class aR per VFD manufacturer table (typically 500 A, 690 V AC); I²t coordinated with VFD bridge withstand. fuses shall be suitable for marine environments, with proper mechanical protection and compliance with relevant standards. | Set | 1
2.11.4.3 | Supply & Installation of Line contactor Supply and installation of Line contactor, 500 A AC-1 rated; provides hard-wired E-stop path independent of VFD. Line contactor shall be suitable for marine environments, with proper mechanical protection and compliance with relevant standards. | Set | 1
2.11.4.4 | Supply & Installation of Earthing and EMC bonding Supply and installation of: - Continuous low-impedance earth path: 120 mm² Cu earth strap from motor frame to VFD enclosure to switchboard earth bar. - Shaft grounding ring on motor: prevents EDM (electric discharge machining) pitting of bearings caused by common-mode bearing currents. - All shall be suitable for marine environments and compliance with relevant standards. | Set | 1
2.12 | L.V CABLES & CABLE WAY
| L.V CABLES - CU / XLPE / PVC: Supply, install, testing and commissionining of complete single or multi-core copper cables including all necessary cleats, supports, brackets, glands, cable terminals, boxes, pipes, excavation, backfilling, and all related accessories and works. All of which shall be according to the specifications, drawings, codes of practice and highest prevailing engineering standards, for the following | Note.
2.12.1 | 4C x 10 sqmm - CU / XLPE / PVC + E=10sqmm (For ICCP System). | L.M | 20
| L.V CABLES From MDB to Transformer Secondary : Supply, install, test and commission low voltage SWA/XLPE / PVC copper cables, (0.6/1K.V) including glands, cable ties, labeling, pipe (Saudi cable or equivalent) in cable tray, PVC pipe suitable size, all fittings (i.e. bends, thrust blocks, end caps, T-connections, reducers, cable glands...etc.), pipes as per drawings, hiding all pipes and cutting for cable pipes, metal lathing 300 mm wide and 3.2 mm thickness shall be nailed and fixed over all grooves, plastering, hiding all cable pipes, ducts, UPVC pipes , excavation, backfilling, laying on ground , Boxes, …etc. All of which shall be according to the specifications, drawings. Codes of practice and highest prevailing engineering standards all associated according to the drawings, specifications and relevant codes of practice and highest prevailing engineering standards such as IEC 60502-1 and BS 6346,XLPE insulated and PVC seathed single or multi core flexible copper cables meeting IEC 60227 and IEC 60502; Cable ends connections are to be made through suitable lugs or terminals, crimped properly & with use of cable glands; for the following: | Note.
2.12.2 | 2 X (4C x 240 sqmm - CU / XLPE / SWA / PVC) + E= 1C X 240 sqmm. | L.M | 15
| L.V CABLES - CU, EMC-screened VFD cable with symmetrical earth conductor: Supply and installation of Cu, EMC-screened VFD cable with symmetrical earth conductor, 360° EMC gland termination at both ends, separate cable tray (300 mm minimum from instrument cables, including all necessary cleats, supports, brackets, glands, cable terminals, boxes, pipes, excavation, backfilling, and all related accessories and works. EMC-screened VFD cable shall be suitable for marine environments and compliance with relevant standards, and shall be according to the specifications, drawings, codes of practice and highest prevailing engineering standards, for the following | Note.
2.12.3 | 2 X ( 4C x 150 sqmm ) + E= 150 sqmm Cu, EMC-screened VFD cable with symmetrical earth conductor (For VFD to Motor Cable). | L.M | 25
| L.V CABLES - From Transformer Secondary to VFD Rectifier Input CU,Cables: Supply, installation, testing, and commissioning of dedicated multi-circuit power cables connecting the secondary phase-shifted outputs of the Isolation Transformer to the input terminals of the 18-Pulse VFD Diode Rectifier: Cable Specification: 0.6/1 kV, flexible/stranded copper conductors, XLPE insulated, flame-retardant PVC sheathed cables, consisting of 3 separate sets of 3-phase circuits (each set phase-shifted by 20 deg), minimum size 3 x 4C x 95 mm2, manufactured to IEC 60502-1.Scope of Work: Complete with high-quality termination kits, heat-shrink sleeves, heavy-duty brass glands, phase identification tags, stainless steel cable ties, arrangement in structured cable trays, complete testing (insulation resistance and phase rotation), and integration with the VFD terminal block. | Note.
2.12.4 | 3 separate sets of 3-phase circuits (each set phase-shifted by 20 deg), Minimum size 3 x (4Cx 95 sqmm). | L.M | 15
| L.V CABLES - Earthing CU,Cables: Supply, install, test and commissioning of complete earthing system including ECC conductors, earth rodes, plates, investigation champer, clamps and all related accessories including bonding and terminations. Earthed equipontential bonding of all exposed and extraneous conductive parts,. All of which shall be according to the technical specifications, drawings, codes of practice and highest prevailing engineering standards. | Note.
2.12.5 | E =1C x 95 sqmm Earthing Conductor for bonding transformer core, VFD cabinet, DBR frame, and cable trays to main earth bar. | L.M | 50
2.13 | SPARE PARTS PROPOSAL & SUBMISSION
2.13.1 | Supply and submission of a detailed spare and consumable parts proposal for all major systems, as recommended by the original equipment manufacturer (OEM) or the system supplier. The proposal shall serve as a pre-approval requisition list for the Port Authority. The scope of this item includes, but is not limited to, the following systems: - Winch Motor System (≥220 kW). - Variable Frequency Drive (VFD) System (≥250 kW). - Impressed Current Cathodic Protection (ICCP) System. - Associated General Consumables and Tools As Lised in Annex_01. | Set | 1
SUB TOTAL DIV-01

## 03-MECH
DIVISION NO.3
BOQ for Mechanical Works of Upgrading of the Main Slipway Winch System
Item NO | DESCRIPTION | UNIT | QTY | UNIT PRICE (USD) | TOTAL COST (USD)
| Preamble 1-General & Interpretation: This Preamble is an integral part of all items in Division 02. It must be read in conjunction with the project's Specifications, Drawings, and individual BoQ item descriptions to define the complete scope, intent, and basis of payment. 2-Site Inspection & Knowledge: The Contractor is deemed to have inspected the site and the existing Slipway Winch system in its "as-is" condition. The Contractor is responsible for all necessary measurements (e.g., shaft diameters, bearing dimensions for Items 3.4 and 3.5) and understanding the full scope prior to pricing. 3-Inclusive Pricing: All entered unit rates and Lump Sum (L.S.) prices are fully inclusive of all costs required for complete execution, including but not limited to: labor, materials, tools, testing, permits, site preparation/access/scaffolding, safety (PPE), waste disposal, and commissioning. No separate payment will be made for ancillary items, incidental works, or logically inferred activities. 4-Compliance with Standards: All works, materials, and methods shall strictly comply with the specific standards cited in each BoQ item description (e.g., BS ISO, BS EN, NFPA). This includes standards for gearboxes, wire ropes, protective coatings, fire suppression systems, and final testing. | Note.
| 5-Contractor's Complete Responsibility: The Contractor is solely responsible for supplying and executing all items and works necessary for a complete, safe, and functional system, even if not explicitly listed. This includes all works implied by the item descriptions, any unforeseen remedial work discovered post-award (e.g., shaft machining per Item 3.4), and integration of all supplied components (e.g., exhaust fans, fire systems, spares). 6-Approvals & Final Acceptance: The Contractor must obtain the Engineer's approval for all materials, shop drawings, and methodologies prior to work commencement. Final payment is contingent upon successful completion of all functional tests, rectification of defects, and submission of all required documentation (as-maintained records, test certificates, warranties, commissioning reports). 7-All training works for all supplied systems under this Contract shall be the sole responsibility of the Contractor. The Contractor shall submit a Training Plan for approval byYGAPC, and upon approval shall carry out and complete all training in accordance with the approved plan. All costs related to training shall be included in the Contract Price. | Note.
3 | MECHANICAL WORKS:
3.1 | Supply, install, test, and commission Tropical T3 inverter high-wall split air-conditioning unit, cooling-only, 3.0 TR nominal capacity, suitable for continuous operation and marine conditions, using zero-ODP, low-GWP refrigerant such as R-32 or approved equivalent. The unit shall include indoor and outdoor units, marine anti-corrosion protection, automatic restart, Lead-Lag interface, supports, anti-vibration mounts, and refrigerant charge. The rate shall include all electrical works from the designated distribution board, including protective devices, local weatherproof isolator, earthing, conduits, power supply cables, and power/control interconnection cables between indoor and outdoor units. It shall also include insulated ASTM B280 copper refrigerant piping installed on a hot-dip galvanized steel service tray, insulated condensate piping connected through an approved trap/air gap to the nearest sanitary drainage point, and all builder’s works, including openings, sleeves, waterproofing, fire-stopping, sealing, patching, and reinstatement of affected finishes, complete for a fully operational installation. | Note.
3.1.1 | HW - 01 - 3.0 TR - Tropical T3 inverter high-wall split air-conditioning unit. | No. | 3
3.2 | Supply, deliver, install, and commission roof-mounted centrifugal exhaust fans with galvanized steel housings protected by a polymeric finish. Fans shall be backward-curved, centrifugal type with direct-drive impeller mounted on a rotating cowl–motor–impeller assembly to allow easy maintenance and removal. Provide external electrical connection box.Provide and fix a roof base support (curb) fabricated from corrosion-resistant steel, finished with polyester powder coat, sized to the fan assembly and including waterproofing flange, fastenings, and vibration isolation pads. Supply and install a bird protection guard (steel mesh) finished with polyester powder coat matching the curb finish.Fans shall be fitted with an asynchronous external-rotor motor with built-in thermal protector, IP55 rating, insulation class F, designed for continuous duty up to 60°C ambient. Standard nominal voltage: 230 V, single-phase, 50 Hz.Include all electrical works required for full operation: power cabling from nearest distribution board, conduits/trunking, cable supports, isolation switch/disconnector, motor starter, terminal connections, earthing/grounding, protective devices, control wiring, labels, testing, and commissioning in accordance with local electrical codes and project specifications.Include all civil/structural works: roof openings, curb fixing and sealing, waterproofing, patching/repair of roof finishes, alignment, and site testing. Provide FAT and site performance test reports (airflow, static pressure, noise, vibration),all works and all other necessary accessories and requirement works to finish this item according to the specifications, and instruction, approval of employer representative... | Note.
3.2.1 | EXF-01-1800 m3/hr | No. | 1
3.3 | Supply, install, test, and commission portable fire extinguishers complete with all required components, accessories, and mounting hardware. Extinguishers shall be factory-new, fully charged, and provided in corrosion-resistant powder-coated cylinders. Units shall include discharge hose/nozzle (as applicable), safety pin with tamper seal, wall mounting bracket, and manufacturer’s identification and operation labels. All extinguishers shall be manufactured, tested, and certified in accordance with the latest editions of BS EN 3 and NFPA 10, and shall comply with the project specifications, drawings, and the Engineer’s approval. | Note.
3.3.1 | ABC Dry Powder Extinguisher – 6 kg | No. | 2
3.3.2 | Carbon Dioxide (CO₂) Fire Extinguisher – 5 kg | No. | 2
3.4 | Providing complete inspection, condition assessment, reporting, and comprehensive maintenance of the slipway winch gearbox, which utilizes a triple-reduction drivetrain system (Worm Gear stage followed by Spur Gear stages), in full compliance with applicable British Standards (BS ISO 10825, BS ISO 281, BS ISO 1328, BS EN 10204). The scope includes: preparing and submitting a technical report for the approval of the Engineer-in-Charge and YGAPC; replacing all bearings as required based on inspection findings; performing weld build-up and precision machining for any component (including worm-gear shafts or gears) exceeding permissible tolerances; completely replacing the gearbox oil with premium German-origin synthetic gear oil (ISO VG 220/320) and providing all necessary materials, labor, tools, consumables, alignment, testing, and commissioning to restore the gearbox to full operational condition. All works shall be performed in accordance with the project drawings and subject to the final inspection and approval of the Engineer-in-Charge and YGAPC. | L.S | 1
3.5 | Supply and delivery of 20 liters of premium German-origin synthetic gear oil, high-temperature resistant, with a viscosity grade of ISO VG 220/320. The oil shall be supplied in original factory-sealed 20-liter containers to ensure proper storage and handling. The supply is intended for use as spare stock for the slipway winch gearbox maintenance and is subject to the final inspection and approval of the Engineer-in-Charge. | No. | 6
3.6 | Carrying out complete maintenance works for the winch, drum, wire rope and gearbox. This item shall encompass all required labor, materials, tools, equipment, testing, and certification to execute a full inspection, thorough cleaning, lubrication, and protective recoating of the entire winch system. All works must comply with the specified British Standards for equipment operating in a high-humidity marine port environment with elevated temperatures. The scope includes: detailed cleaning and surface preparation to a minimum standard of Sa 2½ (BS EN ISO 8501-1); lubrication of all moving parts with approved high-performance, water-resistant (wash-out resistant) marine grease (e.g., Aeroshell Grease 33 or equivalent); and cleaning/lubrication of the wire rope with a penetrating-type corrosion preventive compound compliant with BS ISO 4344 (e.g., Denso Wire Rope Compound or equivalent). Following preparation, all exposed metal surfaces shall be coated with a high-performance epoxy paint system specifically designed for Marine Environment Category C5-M (BS EN ISO 12944) to withstand constant high humidity and salt exposure. The system shall consist of a zinc-rich epoxy primer (BS 4652) and a high-build chemical-resistant epoxy/polyurethane topcoat, applied to a minimum total dry film thickness of 250 microns. A final functional test per BS EN 13135 shall be performed. The lump sum includes all access, staging, waste disposal,r, all works and all other necessary accessories and requirement works to finish this item according to the specifications, and instruction, approval of employer representative. | L.S | 1
3.7 | Supply, installation, testing, commissioning, and certification of a complete UL Listed 4 kg FM-200 (HFC-227ea) direct-application automatic fire suppression system for a Marine Slipway Winch VFD Panel enclosure. The system shall include a dual-activation assembly consisting of a 6 mm stainless-steel thermal detection tube (100°C) installed inside the hazard area and an external manual emergency break-glass release. Upon activation, the system shall instantaneously discharge the FM-200 agent through a stainless-steel (SS304/316) discharge tube network and engineered nozzles to achieve design concentration within 10 seconds. The FM-200 cylinder shall be constructed from SS304, with 14 bar working pressure and 27 bar test pressure, charged with 25 bar N₂ propellant, and fitted with a marine-grade actuation valve. All mounting brackets, supports, fittings, clamps, status indicators, warning labels, and safety devices shall be included all works and,stem shall be designed and installed per NFPA 2001, using FM-200 Clean Agent for Class A, B, and C fires, suitable for marine environments. all other necessary accessories and requirement works to finish this item according to the specifications, and instruction, approval of employer representative. | SET | 1
SUB TOTAL DIV-03

## SUM
United Nations Development Programme (UNDP)
Upgrading of the Main Slipway Winch System at the Seaport of Aden - Aden City
SUMMARY
NO | DESCRIPTION | VALUE | REMARKS.
DIV. 01 | 1-CIVIL & ARCH WORKS. | 0
DIV. 02 | 2-ELECTRICAL WORKS. | 0
DIV. 03 | 3-MECHANICAL WORKS. | 0
TOTAL. |  | 0 | 0

## Annex_1
ANNEX_01 LIST OF SPARE PARTS FOR THE MOTOR, VFD, and ICCP SYSTEM.
Item NO | DESCRIPTION | UNIT | QTY
| PREAMBLE Supply and submission of a detailed spare and consumable parts proposal for all major systems, as recommended by the original equipment manufacturer (OEM) or the system supplier. The proposal shall serve as a pre-approval requisition list for the Port Authority. The scope of this item includes, but is not limited to, the following systems: - Winch Motor System (220 kW, 6-pole, IC416, IE4, ABB; Siemens or equivalent). - Variable Frequency Drive (VFD) System (250 kW, ABB, Siemens; Schneider or equivalent). - Impressed Current Cathodic Protection (ICCP) System. - Associated General Consumables and Tools. | Note.
Supplier's Obligations: List Preparation: The Contractor/Supplier shall prepare a comprehensive list of all recommended spare parts, consumables, and critical tools for each system. The list must be itemized and shall include for each item: Item Number & Description OEM Part Number & Manufacturer Name Technical Specifications Unit of Measure Recommended Quantity for 2-year initial operation Unit Price (USD) Extended Price (USD) Lead Time for Procurement Justification / Purpose (e.g., critical for operation, wear part, consumable, for emergency repair).
Submission for Approval: The complete and priced spare parts list shall be submitted in an editable format (e.g., MS Excel) to the Port Authority's Technical Committee prior to the procurement and delivery of any spare parts. Approval & Selection Rights: The Port Authority reserves the unconditional right to: Review, approve, or reject any item on the list. Select or deselect specific items based on operational priorities and budget considerations. Adjust quantities as deemed necessary. Request clarifications or alternative proposals from the supplier. Procurement & Delivery: Only the items explicitly approved in writing by the Port Authority shall be procured, delivered, and invoiced. All delivered spares must be new, unused, and in original packaging with OEM certificates where applicable. Delivery shall be to a designated storage facility within the Port Authority's premises. Documentation: The supplier shall provide all relevant catalogs, material safety data sheets (MSDS), and storage instructions for the approved spare parts upon delivery.
1 | LIST OF SPARE PARTS FOR THE AC Induction Motor (220kW / 295HP)
1.1 | Carbon Brush Set: Compatible with motor Grounding rings (if applicable), OEM or equivalent | Set | 2
1.2 | Ball/Roller Bearings: Deep groove ball bearing, size: 6316 (or as per motor OEM), C3 clearance, SKF/FAG/NSK | No. | 2
1.3 | Shaft Seal / Gasket Kit: Nitrile rubber or Viton, high-temp resistant, OEM part number or equivalent | Set | 2
1.4 | Terminal Lugs & Connectors: Copper, tin-plated, for 150mm² cable, crimp type | Set | 10
1.5 | Anti-Vibration Pads: Neoprene or rubber, 10mm thickness, suitable for motor base | Set | 4
1.6 | Insulation Varnish / Tape: Class F (155°C) insulation varnish or silicone mica tape | Liter/Roll | 0.5
1.7 | Grease: High-temperature lithium complex grease, NLGI #2, suitable for bearings (e.g., Mobilith SHC 220) | Kg | 5
1.8 | Bolts & Nuts Set: High-tensile steel, M16 x 60mm (or as per motor base), galvanized | Set | 10
2 | LIST OF SPARE PARTS FOR THE VARIABLE FREQUENCY DRIVE (250kW)
2.1 | Cooling Fan Assembly: 24VDC/230VAC fan for cabinet cooling, compatible with ACS880 enclosure | No. | 2
2.2 | Fuses / Circuit Breakers: Semiconductor fuses, 500A, 690V AC, Class aR, for VFD input protection | No. | 3
2.3 | Keypad / Display Unit: local control panel (ACP) or keypad | No. | 1
2.4 | Communication Module: Optional: PROFIBUS DP / Modbus RTU / Ethernet module (as installed) | No. | 1
2.5 | Filter Cards (EMC): RFI filters or du/dt filters if used for long motor cables | No. | 1
2.6 | Cooling Fan Filters: Washable/replaceable air filters for cabinet ventilation | Set | 4
2.7 | 18-Pulse Rectifier Diode Module Set: High-power 3-phase diode bridge rectifier modules/assemblies, rated for 250 kW VFD input, 1200V PIV minimum, heavy-duty marine grade, complete with thermal compound and mounting hardware | Set | 1
2.8 | Dynamic Braking Chopper Module / IGBT: Heavy-duty braking chopper unit/IGBT module for 540V-560V DC bus switching, rated for 250 kW peak braking power, continuous/intermittent duty, OEM part compatible with VFD system. | No. | 1
2.9 | Dynamic Braking Resistor Spare Elements (Resistor Grid Block): High-temperature stainless steel/ceramic resistor element replacement grid set, matching nominal resistance and thermal capacity of the installed 250 kW DBR assembly. | Set | 1
2.10 | DBR Enclosure Forced-Air Cooling Fan Assembly: Marine-grade, high-temperature resistant cooling fan unit (230VAC or 24VDC), IP55/IP66 rated, complete with mounting housing for external DBR cabinet. | No. | 1
2.11 | VFD Main Control & Interface Board (PCBA / Control Unit): Main microprocessor control board with pre-loaded crane/winch firmware macro, conformal coated PCBs for high-humidity marine environment, OEM certified. | No. | 1
2.12 | Phase-Shifting Isolation Transformer Thermal Protection Sensors: Calibrated PT100 / PTC thermistor temperature sensors (3 units set) for monitoring dry-type transformer winding temperature, high-temp lead wires included. | Set | 1
3 | LIST OF SPARE PARTS FOR THE V ICCP (IMPRESSED CURRENT CATHODIC PROTECTION)
3.1 | ICCP Anode: High Silicon Cast Iron (FeSiCr), Ø76mm × 1525mm, with cable | No. | 1
3.2 | Reference Electrode: Ag/AgCl (Silver/Silver Chloride) seawater type, with 10m cable | No. | 2
3.3 | Anode Cable: 10mm² HMWPE/XLPE insulated, UV resistant, tinned copper | L.M | 50
3.4 | Junction Box Seals & Glands: IP68 cable glands (PG16/PG21), silicone sealing gaskets | Set | 10
3.5 | Control Panel Fuse: DC fuse, 10A, for ICCP output circuit | No. | 5
3.6 | Surge Protection Device (SPD): DC surge arrester for ICCP panel, 48VDC | No. | 2
3.7 | Bentonite / Marconite: Earth enhancement material, 25kg bag | Bag | 2
3.8 | Dielectric Isolation Kit: HDPE washers, sleeves, insulating bushes for anode mounting | Set | 2
3.9 | Anti-Corrosion Compound: Copper-based anti-seize, marine grade, 500g tube | Tube | 2
3.10 | Remote Monitoring SIM Card: Prepaid data SIM card for GSM/GPRS module (local network) | No. | 2
4 | LIST OF SPARE PARTS FOR THE PROGRAMMING, DIAGNOSTIC, AND COMMISSIONING TOOL KIT
4.1 | Diagnostic and Testing Equipment: Multifunction Calibrator / Loop Tester: Capable of simulating and measuring 4-20 mA, 0-10V, RTD (PT100), and thermocouple signals. Accuracy: ±0.02% of reading. Complete with test leads, probes, and carrying case. | No. | 1
4.2 | Diagnostic and Testing Equipment: Portable Oscilloscope / Multimeter: 2-channel or 4-channel handheld digital oscilloscope with integrated multimeter functions (Voltage, Current, Resistance, Capacitance, Frequency), Bandwidth: ≥ 100 MHz. Sample rate: ≥ 1 GSa/s. Suitable for diagnosing VFD output waveforms, sensor signals, and control circuit integrity. | No. | 1
4.3 | Diagnostic and Testing Equipment: Insulation Tester / Megger: 1000V insulation resistance tester (Megger) for testing motor winding insulation, cable insulation, and transformer insulation integrity. | No. | 1
4.4 | Diagnostic and Testing Equipment: Protocol Analyzer / Communication Tester: Handheld device capable of analyzing and diagnosing Modbus RTU, Modbus TCP/IP, EtherNet/IP, and PROFIBUS DP communication networks. Identifies communication errors, dropped packets, and network latency issues. | No. | 1